## Design Point
MagCool-DC — Reference Design Point
NSGA-III "knee point" (balanced COP/Qc/cost) design, from results/design_recommendations.txt, section 5
Parameter | Value | Unit | Notes
Peak applied field, μ₀H_max | 1.11 | T | Design variable, NSGA-III Pareto front
Operating frequency, f | 2.592 | Hz | Design variable
Fluid mass flow rate, mdot | 0.4898 | kg/s | Design variable
Regenerator (MCM) mass | 5.31 | kg | Design variable
Regenerator effectiveness, ε | 0.713 | - | Design variable
Particle diameter, d_p | 0.2719 | mm | Packed-bed geometry, co-optimized (geometry_analysis.py)
MCE material / family | La(Fe,Si)13Hy (tuned, Tc=285.3 K) | - | Composition-tuned giant-MCE family, core/cascade.py
Electrical COP, COP_elec | 9.57 | - | Model output at this design point
Average cooling capacity, Qc | 35381.43 | W | Model output at this design point
Derived quantities used to size non-materials hardware
Cooling capacity, Qc | 35.3814 | kW | Qc [W] / 1000
Electrical input power | 3.6971 | kW | Qc [kW] / COP_electrical (same basis as core/economics.py lifetime_cost())
Exact HX duty multiplier | 2.1045 | - | 2 + 1/COP_electrical, exact_hx_duty_multiplier() in core/economics.py
Total heat-exchanger duty | 74.46 | kW | Hot-side duty = Qc + W_elec; total = cold-side + hot-side

## BOM
MagCool-DC — Bill of Materials
Priced with this repo's own bottom-up cost model (core/economics.py: bom_cost() + bottom_up_non_materials_bom()) at the NSGA-III knee-point design point (see 'Design Point' tab). LOW/MID/HIGH = plausible cost band, not a single point estimate — see 'Sources & Assumptions' tab.
# | Category | Component | Sizing / Description | Qty | Unit | Unit Cost Low | Unit Cost Mid | Unit Cost High | Ext. Cost Low | Ext. Cost Mid | Ext. Cost High | Source
MATERIALS (magnet + magnetocaloric material + soft-magnetic yoke — core/economics.py bom_cost())
1 | Materials | NdFeB permanent magnet (N42, ~1.2-1.3 T remanence) | Halbach-type magnet-circuit mass = 13.47 (Rowe 2011 11-device median ratio) x mu0H_max [T] x regenerator mass [kg] | 79.3935 | kg | 40 | 40 | 40 | 3175.7411 | 3175.7411 | 3175.7411 | Bjork, Bahl & Smith, Int. J. Refrig. 34 (2011); mass ratio: Rowe, Int. J. Refrig. 34 (2011), 11-device median (see Sources tab)
2 | Materials | La(Fe,Si)13Hy magnetocaloric material (tuned, Tc = 285.3 K) | Active AMR regenerator bed material; mass = regenerator design variable | 5.31 | kg | 8 | 8 | 8 | 42.48 | 42.48 | 42.48 | Russek & Zimm, Int. J. Refrig. 29 (2006) — literature unit cost for La(Fe,Si)13Hy family
3 | Materials | Soft-magnetic steel (1018) flux-return yoke | Assumed 50% of magnet mass (mid-of-plausible-range placeholder for Halbach/C-core circuits; not a fitted value) | 39.6968 | kg | 5 | 5 | 5 | 198.4838 | 198.4838 | 198.4838 | Silva, Bahl et al., J. Magn. Magn. Mater. 442 (2017) 87-96
[9 empty] | 3416.7049 | 3416.7049 | 3416.7049
NON-MATERIALS HARDWARE (heat exchangers, pump, motor, drive, controls — market-catalog engineering estimate, NOT an AMR-specific vendor quote)
4 | Non-materials | Heat exchangers (hot-side + cold-side, brazed-plate type) | Sized to total HX duty = Qc x (2 + 1/COP_elec) | 74.46 | kW duty | 15 | 30 | 70 | 1116.8997 | 2233.7994 | 5212.1985 | ato.com brazed-plate HX catalog benchmark (~$9-26/kW normalized); Alfa Laval / Bell & Gossett cross-check — see Sources tab
5 | Non-materials | Circulation pump (centrifugal) | Sized to electrical input power = Qc / COP_elec | 3.6971 | kW elec | 150 | 300 | 650 | 554.5679 | 1109.1357 | 2403.1274 | Centrifugal pump cost-estimation rule of thumb ($100-500/HP); ato.com small centrifugal-pump catalog cross-check
6 | Non-materials | Drive motor | Sized to electrical input power | 3.6971 | kW elec | 300 | 600 | 1000 | 1109.1357 | 2218.2715 | 3697.1191 | 2026 motor cost-guide aggregator (avg $600, 1-5 HP); ato.com NEMA induction-motor catalog cross-check
7 | Non-materials | Variable-frequency drive / motor controller | Sized to electrical input power | 3.6971 | kW elec | 100 | 250 | 400 | 369.7119 | 924.2798 | 1478.8476 | Thunder Said Energy "VFDs: the economics?" (avg $250/kW, 15 project case studies); retail VFD catalog cross-check
8 | Non-materials | Controls & enclosure (PLC + NEMA-rated control cabinet) | Fixed allowance — lab/pilot-scale controls do not scale linearly with cooling capacity | 1 | lot | 300 | 800 | 2000 | 300 | 800 | 2000 | industrialmonitordirect.com PLC pricing; e-abel.com enclosure buying guide; KDM Steel / used-equipment catalog data
[9 empty] | 3450.3152 | 7285.4864 | 14791.2927
[9 empty] | 6867.0201 | 10702.1913 | 18207.9976
Note: MID materials cost reproduces this repo's own cost_index() (core/optimize.py) for this design point (~$3,417); LOW=MID=HIGH for materials because bom_cost() uses fixed literature $/kg figures, not a range. Non-materials LOW/MID/HIGH bands are this repo's bottom_up_non_materials_bom() market-catalog engineering estimate for generic component categories at this power class — explicitly NOT an AMR-specific vendor quote (custom manifolding, oscillating-flow seals, and a cycle-synchronized drive could cost more than an off-the-shelf steady-flow component of the same rating). See the 'Sources & Assumptions' tab for full citations.

## Sources & Assumptions
Sources & Assumptions
Condensed from core/economics.py module docstrings (this repo's own cost model).
Design point | results/design_recommendations.txt, section 5 ("RECOMMENDED STARTING DESIGN POINT"), the NSGA-III knee-point design from core/optimize.py's joint field/frequency/flow/material/geometry Pareto search. A starting point, not a final specification.
NdFeB magnet, $40/kg | Bjork, Bahl & Smith, "Determining the minimum mass and cost of a magnetic refrigerator", Int. J. Refrigeration 34 (2011) 1805-1816. Cross-checked by Tura & Rowe (2014), $42/kg NdFeB (Gutfleisch et al. 2010).
Magnet-to-MCM mass ratio, 13.47/T | Rowe, Int. J. Refrig. 34 (2011) Table 1 median across 11 real reported AMR devices (range 3.98-22.65/T); replaces this repo's earlier 2-example Bjork et al. (2011) fit of 3.0/T, which sat at the low end of the real-device range (still reproducible via MAGNET_TO_MCM_MASS_RATIO_PER_TESLA_BJORK2011_LEGACY).
Gd MCM, $20/kg | Bjork et al. (2011); triangulated by Tura & Rowe (2014), $10-20/kg bulk Gd. Not used at this design point (material = La(Fe,Si)13Hy) but is the fallback/proxy price for families with no independently sourced $/kg (see MCM_COST_PER_KG_BY_FAMILY).
La(Fe,Si)13Hy MCM, $8/kg | Russek & Zimm, "Potential for cost effective magnetocaloric air conditioning systems", Int. J. Refrig. 29 (2006) 1366-1373.
Soft-magnetic steel (SMM) yoke, $5/kg, 50% of magnet mass | Silva, Bahl et al., "Permanent magnet design for magnetic heat pumps using total cost minimization", J. Magn. Magn. Mater. 442 (2017) 87-96 (1018 steel flux-return yoke, ~$5/kg). The 50% mass-fraction assumption is an explicitly flagged mid-of-plausible-range placeholder, not a fitted value — no single ratio is reported across this project's literature corpus for a general AMR design.
Heat exchangers, $15-70/kW duty | ato.com 250-plate brazed-plate HX catalog listing (rated 150-450 kW, ~$3,900, implying ~$9-26/kW); Alfa Laval / Bell & Gossett smaller-duty units cross-checked for order of magnitude. HX duty sized via the exact energy balance: total duty = Qc + (Qc + W_elec) = Qc x (2 + 1/COP_electrical).
Pump, $150-650/kW electrical | Centrifugal pump cost-estimation industry reference (Zhilong, 2024), $100-500/HP ($134-670/kW) rule of thumb for small (1-10 HP) industrial units; cross-checked against ato.com's own small centrifugal-pump price list.
Motor, $300-1000/kW electrical | 2026 motor-cost-guide aggregator, $250-2,000 (avg $600) for small (1-5 HP) industrial motors; cross-checked against ato.com NEMA induction-motor catalog and vendor listings for small TEFC motors.
Drive/VFD, $100-400/kW electrical | Thunder Said Energy, "Variable frequency drives: the economics?", average $250/kW from 15 real project case studies; cross-checked against retail VFD catalog pricing (ato.com, gohz.com).
Controls & enclosure, $300-2,000 fixed | PLC pricing (industrialmonitordirect.com, 2026); control-panel-enclosure buying guide (e-abel.com); vendor catalog / used-equipment data (KDM Steel). Treated as a fixed allowance, not $/kW, since lab/pilot-scale control electronics do not scale linearly with cooling capacity.
HONESTY FLAG (repo's own wording) | "This is a market-catalog-based ENGINEERING ESTIMATE for generic component categories at roughly the right duty/power class, not a quote for an actual AMR-specific heat exchanger, pump, or drive (which would need custom manifolding, oscillating-flow-rated seals, a synchronized reciprocating or rotary drive mechanism matched to the AMR cycle frequency, etc., all of which could cost more than an off-the-shelf steady-flow component of the same power rating). It should be read and cited as such — a first bottom-up estimate that genuinely prices the missing hardware categories from real numbers, not as a substitute for an actual AMR-vendor quote or engineering BOM." (core/economics.py, bottom_up_non_materials_bom() section docstring)
What this BOM excludes | Manufacturing/assembly labor, transportation, maintenance, regulatory/certification costs, and the mechanical drive/actuation system that oscillates the field or bed relative to each other (beyond the motor/VFD line items above). See core/economics.py's lifetime_cost() and full_system_cost_estimate_bottom_up() docstrings.